| Technical specification |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Basic information and customer requirements |  |  |  |  | Content of the basic requirements and information |  |  |  |  |  |  |  |  |  |
| 1. Basis for planning and construction |  |  |  |  | The concept of water sector development of Turkmenistan for period 2013-2030 yy |  |  |  |  |  |  |  |  |  |
| 2. Customer |  |  |  |  | Ministry of water sector in Turkmenistan |  |  |  |  |  |  |  |  |  |
| 3. Locus of object |  |  |  |  | Etrap Esenguly Balkan velayat |  |  |  |  |  |  |  |  |  |
| 4. Initial chemical and microbiologic water test |  |  |  |  | Recommendation to specify on place of water intake |  |  |  |  |  |  |  |  |  |
| 5. Planning stage |  |  |  |  | Individual one-stage project |  |  |  |  |  |  |  |  |  |
| 6. Special condition of building |  |  |  |  | Seismicity of building site is not less than 9 points in according with Richter scale |  |  |  |  |  |  |  |  |  |
| 7. Type of building |  |  |  |  | New building |  |  |  |  |  |  |  |  |  |
| 8. General planner |  |  |  |  | Winner of tender |  |  |  |  |  |  |  |  |  |
| 9. Subcontracted planning organisation |  |  |  |  | Institute "Turkmenenergotaslama" of planning Main electric sunstation and *ETL 110kW |  |  |  |  |  |  |  |  |  |
| 10. General subcontracter |  |  |  |  | Winner of tender |  |  |  |  |  |  |  |  |  |
| 11. Subcontracted building organisation |  |  |  |  | Building subdivision in Ministry energetics of Turkmenistan of planning Main electric |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | sunstation and ETL 110kW |  |  |  |  |  |  |  |  |  |
| 12. Years of building |  |  |  |  | 2015-2017 yy |  |  |  |  |  |  |  |  |  |
| 13. Purpose of building |  |  |  |  | Provision with clean drinking water to townships, industrial facility and agricultural areas |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | of etrap Esenguly and Etrek of Balkan velayat |  |  |  |  |  |  |  |  |  |
| 14. Main building and expenses (could be specify |  |  |  |  | 1. Factory of desalination seawater with productivity 50 000 m3\24h |  |  |  |  |  |  |  |  |  |
| while tender, preparing contract documentation |  |  |  |  | 1.1. System of piping in 3 line d-1200mm, long about 2,5km-3,0km and building which provide |  |  |  |  |  |  |  |  |  |
| and project) |  |  |  |  | self-flow withdrawal from Caspian Sea with fish-protecting equipments, system of feed with |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | reagent for disinfection seawater and system of video control inner walls of withdrawal piping |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.2. Receptacle reservoirs initial seawater with heating system in autumn-winter period |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.3. Pumping station with installation of disinfection water |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.4. Extra pumping station which provide withdrawal part of water from receptable reservoirs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | of initial seawater (p.1.2.) with productivity about 0,2m3\sec. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.5. System of piping (diameter is defined by calculating) provides transportation of seawater |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | from extra pumping station to receptable reservoir of initial seawater with size 600 000 m3 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.6. Receptable reservoir of initial seawater with size 600 000 m3, coated with anti-filter protection |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | for provide with water reserve in storm weather to the receptable reservoir of initial seawater (p.1.2.) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.7. Reservoir with sand, special filter and pumping stations. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.8. Production block with instal "reverse osmosis" of desalination seawater, with productivity |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 50 000 m3\24h |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.9. Reservoir of clean water with common size 50 000 m3 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.10. System of discharge buildings which take aside the rest of using seawater |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.11. Transforming station own needs of factory for desalination seawater. Power and quantity |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | of stations is defined with calculating power cunsumption of all factory objects |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.12. Systems of inside-areal supply pipeline of factory desalination seawater (water supply system, |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | sewage system, power supply, installation of telephones) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.13. Production rooms (administrative-domestic building, dining room, laboratory, stock of |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | chemical reagents, checkpoint, stock for keeping reserve parts, repair and engineering workshop) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.14. Chemical reagents for testing of water quality for 3 years of work |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.15. Chemical reagents for desalination seawater for 3 years of work |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.16. Training of personal |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.17. Fence and accomplishment - factory territory has to be max greened with grass and boskets, |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | decorative trees and bushes. For watering green plants there has to be sprinkler and drop system |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | of watering. Inner roads, paths and opened areas have to be concreted, walking paths have to be |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | covered with paving tile or decorative concrete. On the factory territory there have to be |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | illuminating equipments. Territory fence is blind with checkpoint, illuminating by perimeter and |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | instal video observation. There has to be opened parking lot for 25-30 cars. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.18. Delivery of mechanisms, equipments, special auto technics, including: |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | * passenger cars of middle class - 2 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | * minibus with capacity till 15 ppl - 2 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | * tank lorry on basis KAMAZ, size 8 m3 - 1 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | * truck crane with weight-carrying 16 ton - 1 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | * special car of repairing crew "Emergency" - 1 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | * hydrodynamic car - 1 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | * cesspool emptier - 1 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | * dump truck on basis KAMAZ with weight-carrying 20 ton - 1 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | * excavator with capacity of scoop till 0,5 m3 - 1 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | * movable welding machine - 2 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | * movable mobile water pumps with productivity till 250 l\sec - 2 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | * deep-well pump mark *DCW-10 - 4 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 1.19. All equipment for cleaning seawater are planed with 10% power reserve |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Final list and quantity delivered equipment, outfit, special and auto technics will be coordinate |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | by Customer with winner of tender while contract development |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 2. External electric power suply |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 2.1. Substation 110\10-10 kW in according with scheme № 110-4H with ISG-110 kW, |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | with power about 16,5 MVa - 1 pcs |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 2.2. Double-circuit ETL-110 kW Etrek factory Okerem, long 120 km |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3. Pumping station and pressure pipes |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.1. Selection of site for building pumping station, surveying of building site, engineering-geological |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | hydrogeology of building site, hydrogeology calculating. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.2. Planning and building point of building of pumping station with total production 0,6 m3\sec, |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | with max manometric pressure 90m |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.3. Mounting hydromechanical, electrotechnical, crane, secondary equipment and flow meter |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | of pumping station |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.4. Absorbing piping which takes water from clean water reservoir (p.1.9.), pressure pipes |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | in 2 lines to well with flow meter: |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | a) d - 450mm for pressure piping Ekerem-Garadepe-Madaw |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | b) d - 900mm for pressure piping Ekerem-Esenguly-Etrek |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | c) d - 250mm for pressure piping to town Ekerem |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.5. Secondary and domestic objects and buildings for pumping station |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.6. Power supply line 10 kW from main substation "Okerem" to *TS of pumping station, long 0,2km |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.7. Power supply line 6 kW-10 kW (in according with technical specification of power supply) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | from TS to *DRP of pumping station |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.8. Commissioning works and starting test of equipment pumping station |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.9. Transforer substation of own needs, with diesel-generator which provides 100% required |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | power of pumping station, power of substation and diesel-generator is defined by calculating |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | 3.10. Accomplishment of pumping station - territory of pumping station has to be greened with |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | grass and boskets, decorative trees and bushes. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | For watering green plants there has to be sprinkler and drop system of watering. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Inner roads, paths and opened areas have to be concreted, walking paths have to be |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | covered with paving tile or decorative concrete. On the factory territory there have to be |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | illuminating equipments. Territory fence is made with metal net on metal bearing with height |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | not less than 2m with illuminating by all perimeter |  |  |  |  |  |  |  |  |  |
| 13. Requirements to microbiologic, toxicological, |  |  |  |  | Compliance parameters of sanitary and epidemiological requirements Turkmenistan |  |  |  |  |  |  |  |  |  |
| organoleptic indicator and to concentration |  |  |  |  | and TDS 2874-82 "Drinking water" |  |  |  |  |  |  |  |  |  |
| of chemical substances of water received |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| after cleaning |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 14. Work rate of factory desalination seawater |  |  |  |  | 24 hours |  |  |  |  |  |  |  |  |  |
| 15. Common requirements to architectural |  |  |  |  | In according with architectural and planning building. |  |  |  |  |  |  |  |  |  |
| and building, space-and-planning and constructive |  |  |  |  | Constructions of administrative buildings, of checkpoint, of pumping stations reservoirs with |  |  |  |  |  |  |  |  |  |
| solutions |  |  |  |  | clean water has to be done with mass concrete. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Building facades have to be done with using classic architecture elements. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Facade finishing of administrative buildings has to be done with white marble sized 400x800x30mm |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | with mechanical fastening. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Base part of building has to be finished with granite. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Structure of stock workshops, workshops and other production buildings has to be done with |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | steal constructions with bolt connection, outer finishing has to be done with sandwish-panels |  |  |  |  |  |  |  |  |  |
| 16. Start terms of planning, building-mounting |  |  |  |  | Emmediately after publishing tender winner |  |  |  |  |  |  |  |  |  |
| works and delivery work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 17. Finish terms of all works |  |  |  |  | In according with President Resolution of Turkmenistan |  |  |  |  |  |  |  |  |  |
| 18. Finish terms of project planning for all |  |  |  |  | Not later that 12 months after publishing tender winner |  |  |  |  |  |  |  |  |  |
| work complex |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 19. Term of representation contract to Customer |  |  |  |  | Not later than 1 month after publishing tender winner |  |  |  |  |  |  |  |  |  |
| 20. Terms of delivery equipment |  |  |  |  | Not later than 6 months till the end of finishing all works |  |  |  |  |  |  |  |  |  |
| 21. Delivered equipments |  |  |  |  | New, not earlier than 2015 year of production |  |  |  |  |  |  |  |  |  |
| 22. Basic requirements to delivered equipments |  |  |  |  | Delivered equipments have to be the newest technologies of famous world brands, max automatical, |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | with security systems in the moments of sudden stop or failure of fixed parameters. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Provide delivery and mounting system of controller and data collection, system of technological |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | record desalinated water on way out from system for direction of technological process of |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | desalination plant in content of delivered equipment. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Provide delivery and mounting of autonomous inner-object radio connection system and |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | fire alarm system. |  |  |  |  |  |  |  |  |  |
| 23. Secondary requirements to equipments |  |  |  |  | Deliverers have to provide documents which confirm quality of derivered mechanical equipments |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | and auto machines, also their safety while work productions |  |  |  |  |  |  |  |  |  |
| 24. Warranty period of serve for eqiupments |  |  |  |  | Not less than 3 years |  |  |  |  |  |  |  |  |  |
| and mechanisms |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 25. Warranty period of no-failure operation |  |  |  |  | Not less than 3 years |  |  |  |  |  |  |  |  |  |
| for equipment and mechanisms |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26. Secondary requirements for pipes used while |  |  |  |  | Delivered pipes of pressure piping should have inner and outer anticorrosive isolation. |  |  |  |  |  |  |  |  |  |
| building |  |  |  |  | All pipe bandins "Reverse osmosis" have to be done with high-strength rustproof steal |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | or appropriate polymer materials. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Pumping and distribution pipes and lock valves have to be steady to seawater. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | All outer pipings should have multi-layer thermic isolation |  |  |  |  |  |  |  |  |  |
| 27. Secondary requirements to concretes used |  |  |  |  | All concrete used in constructions has to be done with using appropriate additions which increase |  |  |  |  |  |  |  |  |  |
| in building |  |  |  |  | waterproof, frost- and salt -proof. |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Concrete constructions which are touched with seawater (bottom and walls of reservoirs, discharge |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | and water taking channels) or which are exposed to influence of atmospheric precipitations |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | (roads, paths, road border) should have extra isolation which excludes premature demage of concrete |  |  |  |  |  |  |  |  |  |
| 28. Requirements for environment defence |  |  |  |  | In according with *BNT |  |  |  |  |  |  |  |  |  |
| 29. Fire preventions and warning about |  |  |  |  | In according with BNT |  |  |  |  |  |  |  |  |  |
| emergency situations |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Notes: |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | *ETL - electricity transmition line |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | *TS - transformer substation |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | *DCW - driven by motror, centrifugal, for water supply |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | *BNT - building norms of Turkmenistan |  |  |  |  |  |  |  |  |  |  |  |  |  |